## Sheet1
ID | Conduit Name | Zones | Purdue Layer | Protocols | Sec_Protocol | Has_Enc | Auth_Type | Has_Int | Sec_Placement | DATA Type | C_level | A_level | I_level | S_level | Business impact | Data Lifetime | Contains PII? | Exposure | Device | Firmware upgradable | Crypto modifiable | Vendor Support of PQC | Expert Feedback: Recommended PQC | Expert Feedback: Recommended PQC Why | Expert Feedback: Deployed CAT | Expert Feedback: Deployed CAT Why | Expert Feedback: CAT Justification | Expert Feedback: CAT Justification Why | Expert Feedback: Feasibility | Expert Feedback: Feasibility Why | Expert Feedback: Migration Priority | Expert Feedback: Migration Priority Why | Expert Feedback: Overall | Expert Feedback: Overall Why | Expert Feedback: Comments
C1 | Spot Market ↔ Energy Market Subsystem | Market – Energy Market Subsystem | L5–L4 | WebService, Internet, phone call | TLS 1.2/1.3 (sometimes plus VPN/IPsec) | Yes | ServerCert | Yes | EndToEnd (optionally also Gateway/VPN) | Market bids, schedules, prices, contracts | H | H | H | M | High | 5–10y | No | Internet / external B2B (High) | Market systems, EMS/market servers | Y | Y | N/Unknown
C2 | Energy Market Subsystem ↔ DMS | Energy Market – Grid Operation | L4–L3 | WebService or Email | TLS 1.2/1.3 (for WebService), TLS for SMTP + optional S/MIME | Yes | ServerCert (sometimes Password for mail) | Yes | EndToEnd (often also inside VPN) | Operational plans, schedules, outage & congestion info | M | H | H | M | High | ~5–10y | No | Utility WAN / extranet (Medium) | EMS / DMS application servers | Y | Y | N/Unknown
C3 | Energy Market Subsystem ↔ MDMS | Energy Market – Metering | L4–L3 | WebService or Email | TLS 1.2/1.3 (often via VPN) | Yes | ServerCert | Yes | EndToEnd (plus VPN tunnel) | Aggregated metering and settlement data | H | M | H | L | High | 10y+ | No / Possible | Utility WAN (Medium) | MDMS servers | Y | Y | N/Unknown
C4 | SCADA System ↔ Automation Headend | Grid Operation | L3–L3 | IEC 60870-5-104, IEC 61850 over Ethernet | IPsec ESP (site-to-site), sometimes None in legacy | Yes (where IPsec is used), No (legacy) | MutCert (site-to-site VPN) | Yes (ESP auth / AEAD) | GatewayOnly (between routers, not inside 104/61850) | Real-time telemetry, alarms, control commands | M | H | H | H | High | Telemetry days, logs 5+ years | No | Utility WAN (Medium) | SCADA master, automation headend servers | Y | Y | N/Unknown
C5 | DMS ↔ Automation Headend | Grid Operation | L3–L3 | IEC 60870-5-104, IEC 61850, WebService/Ethernet | IPsec ESP (site-to-site) | Yes | MutCert | Yes | GatewayOnly | Switching plans, setpoints, topology data | M | H | H | H | High | ~5–10y | No | Utility WAN (Medium) | DMS & automation headend servers | Y | Y | N/Unknown
C6 | AMI Headend ↔ MDMS | Metering | L3–L3 | WebService over Ethernet | TLS 1.2/1.3 | Yes | MutCert (server + client certs) | Yes (AEAD or MAC) | EndToEnd | Meter readings, events, billing data, remote disconnect commands | H | M | H | L–M | High | 7–10y | Yes | Utility WAN / data centre network (Medium) | AMI headend, MDMS servers | Y | Y | N/Unknown
C7 | Automation Headend ↔ Automation Frontend | Grid Operation – Station | L3–L2 | IEC 60870-5-104, IEC 61850, WebService over Ethernet, field radio, WiMAX, PLC | IPsec ESP (typical), sometimes None / MAC-only | Yes (when IPsec enabled) | MutCert | Yes | GatewayOnly (WAN/radio edge) | Substation status, control commands, configuration | M | H | H | H | High | Years (event logs, switching records) | No | Long-distance WAN / wireless (High) | Automation frontend (RTU/IED gateway) | Maybe | Maybe | N
C8 | Automation Frontend ↔ Primary Substation Node | Primary Substation (high/medium voltage) | L2–L2 | IEC 60870-5-104, IEC 61850, WebService Ethernet | None | Partial (Yes where MACsec/VPN used, No otherwise) | None (or link-layer keys in MACsec) | Partial | LAN-only (inside substation) | Breaker status, measurements, control | M | H | H | H | High | Logs 5+ years | No | Substation LAN (Low–Medium) | Substation controller / bay controllers (Resource Constrained) | Maybe | Maybe | N
C9 | Primary Substation Node ↔ Local I/O | Primary Substation – Process | L1–L0 | Modbus RS485, IEC 61850 Ethernet, analog loops | None | No | None | No | None (physical isolation only) | Raw sensor data, breaker trips/close commands | L | H | H | H | High | Real-time, logs <1y | No | Local wired network (Low) | IEDs, sensors, actuators (Resource Constrained) | Limited/Maybe | No | N
C10 | Secondary Substation Node / Concentrator ↔ Smart Meter | Secondary Substation (med/low volt.) – Customer Premises / Metering | L2–L1 | G3-PLC, PRIME, CX1, LonTalk over PLC; DLMS/COSEM on higher layer | DLMS/COSEM security (AES) | Yes | PSK / shared symmetric keys (per meter or per group) | Yes (DLMS MAC) | EndToEnd (between meter and headend/concentrator) | Meter readings, events, tariff & disconnect commands | H | M | M–H | L–M | High | 7–10y | Yes | Field PLC over public LV grid (High) | Smart meters (Resource Constrained), concentrators | Often Y | Limited | N
C11 | Smart Grid Gateway (Customer Premises) ↔ Home Automation | Customer Premises | L1–L1 | WebService over coax / Ethernet | TLS 1.2 (or vendor TLS) | Yes | ServerCert (sometimes PSK/device token) | Yes | EndToEnd | Home energy management commands, consumption info | H | M | M | L | Medium | 1–5y | Yes | Customer LAN (High, under user control) | Home energy gateway, home automation controller | Y | Limited | N
C12 | Smart Meter / Home Automation ↔ Controllable Loads | Customer Premises – Process | L1–L0 | Analog, LON, BacNet, EIB, WLAN (wired/wireless) | None | Partial (Yes on Wi-Fi, No on fieldbus) | PSK (Wi-Fi) / None (fieldbus) | Partial (Wi-Fi has integrity, fieldbus mostly not) | LocalOnly (in-home) | Device setpoints, schedules, usage data | H | M | M | M | Medium | 1–2y | Yes (indirectly) | In-home fieldbuses / Wi-Fi (High) | Smart appliances, controllable loads | Maybe | No/limited | N
C13 | E-Mobility Management ↔ Charging Station | E-Mobility | L3–L1 | XML over HTTP, Ethernet; OpenChargePoint Protocol, IEC 61334, GPRS/UMTS (wired & cellular) | TLS 1.2 (sometimes + VPN) | Yes | ServerCert or MutCert (depends on operator) | Yes | EndToEnd (often plus VPN) | Charging control, tariffs, billing records, station status | H | M | M | M | High | 5y+ | Yes | Internet / cellular (High) | Charging station back-end & local controller | Y | Maybe | N
C14 | Charging Station ↔ E-Vehicle | E-Mobility – Customer / Process | L1–L0 | IEC 61851 PLC, IEC 15118 PLC | TLS 1.2 (IEC 15118 sessions), None for pure 61851 signalling | Partial | ServerCert / MutCert (Plug&Charge) | Partial | EndToEnd (between EV and EVSE for 15118) | Charging authorisation, contract identifier, charging status | H | M | M | M–H | High | ~5y | Yes | Local physical connection (Low–Medium) | EVSE (charger) and EV on-board system | Y | Limited | N
C15 | Smart Grid Gateway (Building) ↔ Building Management | Smart Building | L3–L2/L1 | WebService over Ethernet | TLS 1.2/1.3 | Yes | ServerCert | Yes | EndToEnd | Building energy optimisation, consumption profiles | M | M | M | M | Medium | 1–5y | Typically No (organisation-level) | Building LAN (Medium) | Building smart-grid gateway & BMS server | Y | Y | N
C16 | Building Automation ↔ HVAC / Lighting | Smart Building – Process | L1–L0 | LON, BacNet, EIB (wired, sometimes wireless) | None | No | None | No | None (depends on physical/logical isolation) | Local control commands, temperatures, occupancy signals | L–M | M | M | M | Medium | <2y | No (unless detailed occupancy logged elsewhere) | Building fieldbus (Low–Medium) | HVAC & lighting controllers (Resource Constrained) | Maybe | No | N